## Sheet1
Description | PLC Tag Name | Modbus Register | Data Type | Scaling | Unit | Type
Chamber #1 High Temperature Alarm Bit | TAH121B | 1 | BOOL | None | None | Input to Delta
Chamber #1 High Temperature Alarm Bit | TAH121B | 1.01 | BOOL | None | None | Input to Delta
TSHH121A - Ch 1 TSHH122A - Ch 2 High Limits Alarm | ChamberHighLimitsAlarm | 1.02 | BOOL | None | None | Input to Delta
High Cold Face #1 Temperature Warning Alarm Bit | TAH127A | 1.03 | BOOL | None | None | Input to Delta
High Cold Face #2 Temperature Warning Alarm Bit | TAH128A | 1.04 | BOOL | None | None | Input to Delta
Cold Face #1 High Temperature Alarm Bit | TAHH127A | 1.05 | BOOL | None | None | Input to Delta
Cold Face #2 High Temperature Alarm Bit | TAHH128A | 1.06 | BOOL | None | None | Input to Delta
System Ready Temperature Lost Alarm Bit | TAL124 | 1.07 | BOOL | None | None | Input to Delta
Process Inlet Pressure Deviation Low Alarm Bit | PAL101 | 1.08 | BOOL | None | None | Input to Delta
System High Differential Air Flow Fault | PDAH103B | 1.09 | BOOL | None | None | Input to Delta
System Low Differential Air Flow Fault | PDAL103A | 1.1 | BOOL | None | None | Input to Delta
OK to Modulate Firing Rate | Modulate | 1.11 | BOOL | None | None | Input to Delta
Heat Recovery Alarms Combined | HeatRecoveryAlarms | 1.12 | BOOL | None | None | Input to Delta
HeatRecoveryEnabled | HeatRecoveryEnabled | 1.13 | BOOL | None | None | Input to Delta
Spare | --- | 1.14 | BOOL | None | None | Input to Delta
Spare | --- | 1.15 | BOOL | None | None | Input to Delta
Spare | --- | 1.16 | BOOL | None | None | Input to Delta
Spare | --- | 1.17 | BOOL | None | None | Input to Delta
Spare | --- | 1.18 | BOOL | None | None | Input to Delta
Spare | --- | 1.19 | BOOL | None | None | Input to Delta
Spare | --- | 1.2 | BOOL | None | None | Input to Delta
Spare | --- | 1.21 | BOOL | None | None | Input to Delta
Spare | --- | 1.22 | BOOL | None | None | Input to Delta
Spare | --- | 1.23 | BOOL | None | None | Input to Delta
Spare | --- | 1.24 | BOOL | None | None | Input to Delta
Spare | --- | 1.25 | BOOL | None | None | Input to Delta
Spare | --- | 1.26 | BOOL | None | None | Input to Delta
Spare | --- | 1.27 | BOOL | None | None | Input to Delta
Spare | --- | 1.28 | BOOL | None | None | Input to Delta
Spare | --- | 1.29 | BOOL | None | None | Input to Delta
Spare | --- | 1.3 | BOOL | None | None | Input to Delta
Spare | --- | 1.31 | BOOL | None | None | Input to Delta
Burner Gas Firing Rate Valve A Commanded Open Percent | TCV210A_PercentOpen | 5 | DINT | None | Percent | Input to Delta
Burner Gas Firing Rate Valve B Commanded Open Percent | TCV210B_PercentOpen | 9 | DINT | None | Percent | Input to Delta
RTO Inlet Pressure | PIC101.PV | 13 | DINT | x100 | Inches Water Column | Input to Delta
RTO Inlet Pressure Setpoint | PIC101.SP | 17 | DINT | x100 | Inches Water Column | Input to Delta
Controlled Shutdown Temperature Setpoint | ShutdownTemp | 21 | DINT | None | Deg F | Input to Delta
RTO Fresh Air Damper Commanded Open Percent | TCV400_PercentOpen | 25 | DINT | None | Percent | Input to Delta
Fresh Air Cooling Setpoint | TIC400_Chamber_SP | 29 | DINT | None | Deg F | Input to Delta
Chamber #1 Temperature | TE121B | 33 | DINT | None | Deg F | Input to Delta
Chamber #2 Temperature | TE122B | 37 | DINT | None | Deg F | Input to Delta
RTO System Fan Actual Frequency | VFD105_SPEEDHz | 41 | DINT | x100 | Hz | Input to Delta
Outdoor Air Temperature Setpoint | TE1_SP | 45 | DINT | None | Deg F | Input to Delta
Supply Air Temperature Setpoint | TIC2.SP | 49 | DINT | None | Deg F | Input to Delta
Stack Pressure Setpoint | PIC1.SP | 53 | DINT | x100 | Inches Water Column | Input to Delta
Supply Fan Commanded Frequency | VFD2_SpeedRefHz | 57 | DINT | x100 | Hz | Input to Delta
Exhaust Fan Commanded Frequency | VFD1_SpeedRefHz | 61 | DINT | x100 | Hz | Input to Delta
Stack Pressure | PIC1.PV | 65 | DINT | x100 | Inches Water Column | Input to Delta