## Modbus GS 5.8.1.7
| Modbus Parameter name | Modbus Addr. | Range(from manual) | Format | R/W | Descriptions | Tested V5.8.x.x
1 | Manual Capacity | 40002 | 20-100% | INTEGER | WRITE/READ | Manual Capacity | ok
2 | Setpoint Channel 1 | 40003 | 0-95% | INTEGER | WRITE/READ | Sets the desired humidity setpoint value for Ch1 | ok
3 | Setpoint Channel 2 | 40004 | 10-95% | INTEGER | WRITE/READ | Sets the humidity high limit setpoint value for Ch2 | ok
4 | Digital RH/Demand Ch1 | 40005 | 0-100% | INTEGER | WRITE/READ | Actual humidity or demand via BACnet Ch1 | ok
5 | Digital RH/Demand Ch2 | 40006 | 0-100% | INTEGER | WRITE/READ | Actual humidity or limiter via BACnet Ch2 | ok
6 | Band Channel 1 | 40017 | 6-65% | INTEGER | WRITE/READ | P-band (proportional band) | ok
7 | Band Channel 2 | 40018 | 6-65% | INTEGER | WRITE/READ | P-band (proportional band) limiter | ok
8 | Itime Channel 1 | 40021 | 1-60min | INTEGER | WRITE/READ | Integral time channel 1 | ok
9 | Damp Channel 2 | 40022 | 1-60sec | INTEGER | WRITE/READ | Damp time channel 2 | ok
10 | Status | 30003 | 0.-22 | INTEGER | READ | Operating status | ok
|  |  |  | INTEGER | READ | 0-HUMIDIFYING | ok
|  |  |  | INTEGER | READ | 1-IDLE | ok
|  |  |  | INTEGER | READ | 2-IDLE DRAIN | ok
|  |  |  | INTEGER | READ | 3-KEEP WARM | ok
|  |  |  | INTEGER | READ | 4-FILLING | ok
|  |  |  | INTEGER | READ | 5-DRAINING | ok
|  |  |  | INTEGER | READ | 6-DISABLED | ok
|  |  |  | INTEGER | READ | 7-SAFETY LOOP | ok
|  |  |  | INTEGER | READ | 9-STOPPED | ok
|  |  |  | INTEGER | READ | 10-BLOWER PACK | ok
|  |  |  | INTEGER | READ | 11-FILL CHECK | ok
|  |  |  | INTEGER | READ | 12-FTBD | ok
|  |  |  | INTEGER | READ | 13-Warning_Humidifying | ok
|  |  |  | INTEGER | READ | 14- Warning_Idle | ok
|  |  |  | INTEGER | READ | 15- Warning_Idle_Drain | ok
|  |  |  | INTEGER | READ | 16- Warning_Keepwarm | ok
|  |  |  | INTEGER | READ | 17-Warning_Filling | ok
|  |  |  | INTEGER | READ | 18-Warning_Draining | ok
|  |  |  | INTEGER | READ | 19-Warning_Float_Check | ok
|  |  |  | INTEGER | READ | 20-Warning_FTBD | ok
11 | Channel 1 | 30004 | 0-100% | INTEGER | READ | Input signal channel 1 | ok
12 | Channel 2 | 30005 | 0-100% | INTEGER | READ | Limiter signal channel 1 | ok
13 | System Demand | 30006 | 0-100% | INTEGER | READ | System Demand | ok
14 | Safety Loop | 30007 | 0 OR 1 | INTEGER | READ | External safety chain | ok
15 | Operating hours | 30100 | 0-5000HRS | FLOAT AB CD | FLOAT AB CD | Operating hours | ok
16 | Max.Capacity output | 31200 | lb/hrs | INTEGER | READ | Max.Capacity | ok
17 | Actual Capacity | 31201 | lb/hrs | INTEGER | READ | Unit's Capacity | ok
18 | Primery Inlet V1 | 31202 | 0 OR 1 | INTEGER | READ | Primary Fill Valve 1 | ok
19 | Primery Inlet V2 | 31203 | 0 OR 1 | INTEGER | READ | Secondary Fill Valve 1 | ok
20 | Secondery Inlet V1 | 31204 | 0 OR 1 | INTEGER | READ | Drain Water Cool Valve | ok
21 | Secondery Inlet V2 | 31205 | 0 OR 1 | INTEGER | READ | Primary Fill Valve 2 | ok
22 | Drain | 31206 | 0 OR 1 | INTEGER | READ | Drain pump | ok
23 | Error Code | 31208 | Operational manual fault | INTEGER | READ |  | ok
[6 empty] | 1-Smartcard | ok
[6 empty] | 10 -Controller | ok
[6 empty] | 22-Fill Timeout | ok
[6 empty] | 28-Service Reminder Fault | ok
[6 empty] | 46-Drain Check | ok
[6 empty] | 84-Driver Board A/B | ok
[6 empty] | 138-Over Temperature | ok
[6 empty] | 139-No Burners Available via Software | ok
[6 empty] | 140-Keep Warm | ok
[6 empty] | 142-No Burners Available | ok
[6 empty] | 143- Illegal Gas Valve Activated | ok
[6 empty] | 144-Float Level | ok
[6 empty] | 145-Fill Check | ok
[6 empty] | 146-Blower Not Operating | ok
[6 empty] | 150-Air Proving switch open | ok
[6 empty] | 153-AP Exhaust | ok
24 | Low float level | 31209 | 0-Low Float Level | INTEGER | READ | 0-Low Float Level | ok
25 | Mid float level | 31210 | 1-Mid Float Level | INTEGER | READ | 1-Mid Float Level | ok
26 | High float level | 31211 | 2-High Float Level | INTEGER | READ | 2-High Float Level | ok

## Bacnet GS 5.8.1.7 Embedded
| Object-Name | Object-ID | Modbus Addr. | Description | Range | R/W | Comments
1 | Safety Loop | 3 | 30007 | External safety chain | 0 OR 1 | READ
2 | Status | 614 | 30003 | Operating status | 0.-22 | INTEGER | READ
[5 empty] | 1-HUMIDIFYING | INTEGER | READ
[5 empty] | 2-IDLE | INTEGER | READ
[5 empty] | 3-IDLE DRAIN | INTEGER | READ
[5 empty] | 4-KEEP WARM | INTEGER | READ
[5 empty] | 5-FILLING | INTEGER | READ
[5 empty] | 6-DRAINING | INTEGER | READ
[5 empty] | 7-DISABLED | INTEGER | READ
[5 empty] | 8-SAFETY LOOP | INTEGER | READ
[5 empty] | 10-STOPPED | INTEGER | READ
[5 empty] | 11-BLOWER PACK | INTEGER | READ
[5 empty] | 12-FILL CHECK | INTEGER | READ
[5 empty] | 13-FTBD | INTEGER | READ
[5 empty] | 14-Warning_Humidifying | INTEGER | READ
[5 empty] | 15- Warning_Idle | INTEGER | READ
[5 empty] | 16- Warning_Idle_Drain | INTEGER | READ
[5 empty] | 17- Warning_Keepwarm | INTEGER | READ
[5 empty] | 18-Warning_Filling | INTEGER | READ
[5 empty] | 19-Warning_Draining | INTEGER | READ
[5 empty] | 19-Warning_Float_Check | INTEGER | READ
[5 empty] | 20-Warning_FTBD | INTEGER | READ
3 | Channel 1 | 10001 | 30004 | Input signal channel 1 | 0-100% | INTEGER | READ
4 | Channel 2 | 10002 | 30005 | Limiter signal channel 2 | 0-100% | INTEGER | READ
5 | System Demand | 10057 | 30006 | System Demand | 0-100% | INTEGER | READ
6 | Operating hours | 10060 | 30100 | Operating hours | 0-5000HRS | FLOAT | READ
7 | Digital RH/Demand Ch1 | 10044 | 40005 | Actual humidity or demand via BACnet Ch1 | 0-100% | INTEGER | WRITE/READ
8 | Digital RH/Demand Ch2 | 10045 | 40006 | Actual humidity or limiter via BACnet Ch2 | 0-100% | INTEGER | WRITE/READ
9 | Manual Capacity | 10008 | 40002 | Manual Capacity | 0-100% | INTEGER | WRITE/READ
10 | Setpoint Channel 1 | 10010 | 40003 | Sets the desired humidity setpoint value for Ch1 | 0-95% | INTEGER | WRITE/READ
11 | Band Channel 1 | 10011 | 40017 | P-band (proportional band) | 6-65% | INTEGER | WRITE/READ
12 | ITime Channel 1 | 10012 | 40021 | Integral time channel 1 | 1-60 min | INTEGER | WRITE/READ
13 | Setpoint Channel 2 | 10013 | 40004 | Sets the humidity high limit setpoint value for Ch2 | 10-95% | INTEGER | WRITE/READ
14 | Band Channel 2 | 10014 | 40018 | P-band (proportional band) limiter | 6-65% | INTEGER | WRITE/READ
15 | Damp Channel 2 | 10015 | 40022 | Damp time channel 2 | 0-60 s | INTEGER | WRITE/READ
16 | Max.Capacity output | 10100 | 31200 | Max.Capacity | 0-100% | INTEGER | READ
17 | Actual Capacity | 10103 | 31201 | Unit's Capacity | 0-100% | INTEGER | READ
18 | Primery Inlet V1 | 599 | 31202 | Primary Fill Valve 1 | 0 OR 1 | INTEGER | READ
19 | Primery Inlet V2 | 601 | 31203 | Secondary Fill Valve 1 | 0 OR 1 | INTEGER | READ
20 | Secondery Inlet V1 | 603 | 31204 | Drain Water Cool Valve | 0 OR 1 | INTEGER | READ
21 | Secondery Inlet V2 | 605 | 31205 | Primary Fill Valve 2 | 0 OR 1 | INTEGER | READ
22 | Drain | 504 | 31206 | Drain pump | 0 OR 1 | INTEGER | READ
23 | Low float level | 546 | 31209 | 0-Low Float Level | 0 OR 1 | INTEGER | READ
24 | Mid float level | 544 | 31210 | 1-Mid Float Level | 0 OR 1 | INTEGER | READ
25 | High float level | 542 | 31211 | 2-High Float Level | 0 OR 1 | INTEGER | READ
26 | Error Code | 10730 | 31208 | Operational Manual Fault | 0-999 | INTEGER | READ
[5 empty] | 1-Smartcard |  | READ
[5 empty] | 10 -Controller |  | READ
[5 empty] | 22-Fill Timeout |  | READ
[5 empty] | 28-Service Reminder Fault |  | READ
[5 empty] | 46-Drain Check |  | READ
[5 empty] | 84-Driver Board A/B |  | READ
[5 empty] | 138-Over Temperature |  | READ
[5 empty] | 139-No Burners Available via Software |  | READ
[5 empty] | 140-Keep Warm |  | READ
[5 empty] | 142-No Burners Available |  | READ
[5 empty] | 143- Illegal Gas Valve Activated |  | READ
[5 empty] | 144-Float Level |  | READ
[5 empty] | 145-Fill Check |  | READ
[5 empty] | 146-Blower Not Operating |  | READ
[5 empty] | 150-Air Proving switch open |  | READ
[5 empty] | 153-AP Exhaust |  | READ